## Sheet1
BU | Building Location | Address | Batch | Building SQFT | Year Built | Estimated Rooftop PV System Size (kW DC) | Estimated Rooftop PV System Size (kW AC)
MON7003 | Montreal, QC | 2580 Dollard Avenue | 1 | 89000 | 1973 | 1113.12 | 695.7
MON7017 | Lachine, QC | 1600 50th Avenue | 1 | 241599 | 1968 | 3402.8 | 2126.75
MON7020 | Pointe-Claire, QC | 5500 Trans-Canada Highway | 1 | 511848 | 1958 | 5900.26 | 3687.6625
MON7024 | Pointe-Claire, QC | 117 Hymus Boulevard | 1 | 211346 | 2004 | 2789.865 | 1743.6656
MON7025 | Montreal, QC | 7101 Notre-Dame Street East | 1 | 611434 | 1947 | 6739.47 | 4212.1687
MON7026 | Dorval, QC | 2900 Avenue Andre | 1 | 111103 | 1975 | 1436.288 | 897.68
MON7027 | Montreal, QC | 7350 Trans-Canada Highway | 1 | 115000 | 1972 | 1122.3 | 701.4375
MON7028 | Saint-Laurent, QC | 2520 Marie-Curie | 1 | 154374 | 1990 | 1951.67 | 1219.7938
MON7030 | Dorval, QC | 1177-1185 55e Ave | 1 | 155892 | 1990 | 1929.42 | 1205.8875
MON7038 | Montreal, QC | 5685 Rue Cypihot | 1 | 157208 | 1980 | 2044.305 | 1277.6906
MON7043 | Saint-Laurent, QC | 3665 Boulevard Poirier | 1? | 534111 | 2003 | 6100.92 | 3813.075
MON7044 | Pointe-Claire, QC | 7800 Transcanada | 1 | 68093 | 1964 | 4547.07 | 2841.9188
21025 | Montreal | 8000 Blaise-Pascal | 1 | 326345 | 1993 | 2392.2 | 1495.125
21027 | Laval | 1313 Autoroute Chomedey | 1 | 165000 | 1999 | 2241.27 | 1400.7938
21051 | Lachine | 1125 50th Avenue | 1? | 210710 | 2000 | 2168.86 | 1355.5375
21226 | Montreal | 5000 rue Fairway & 1645 50e Avenue | 1 | 108292 | 1978 | 1197.38 | 748.3625
21229 | Montreal | 333 Chemin du Tremblay | 1 | 86842 | 1987 | 1134.965 | 709.3531
21230 | Montreal | 1500 rue Nobel | 1 | 82051 | 1989 | 1050.39 | 656.4937
21231 | Montreal | 2000 32e Avenue | 1 | 81288 | 1985 | 1074.83 | 671.7687
21317 | Montreal | 1825 - 1865 32e Avenue | 1 | 71616 | 1986 | 1444.23 | 902.6437
21318 | Montreal | 1876 - 1936 32e Avenue | 1 | 84659 | 1987 | 1114.635 | 696.6469
21319 | Longueuil | 2350 de la Province | 1? | 222464 | 1967 | 2757.85 | 1723.6562
21344 | Montreal | 2995 Le Corbusier | 1 | 130736 | 1975 | 1506.89 | 941.8062
21383 | Montreal | 700 McCaffrey Road | 1 | 79875 | 1975 | 1082.145 | 676.3406
21390 | Montreal | 401 Rue Marie Curie | 1 | 753072 | 2005 | 9767.52 | 6104.7
21391 | Montreal | 3055 Rue Anderson | 1 | 365694 | 2003 | 4860.996 | 3038.1225
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will likely need to upsize inverter capacity to meet 0.7MW minimum
Note on H7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will likely need to upsize inverter capacity to meet 0.7MW minimum
Note on H8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will likely need to upsize inverter capacity to meet 0.7MW minimum
Note on H17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will likely need to upsize inverter capacity to meet 0.7MW minimum
Note on H18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will likely need to upsize inverter capacity to meet 0.7MW minimum
Note on H19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will likely need to upsize inverter capacity to meet 0.7MW minimum
Note on H20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will likely need to upsize inverter capacity to meet 0.7MW minimum
Note on H22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will likely need to upsize inverter capacity to meet 0.7MW minimum
Note on H25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will likely need to upsize inverter capacity to meet 0.7MW minimum

## Sheet2
| BU | MON7003 | MON7017 | MON7020 | MON7024 | MON7025 | MON7026 | MON7027 | MON7028 | MON7030 | MON7038 | MON7043 | MON7044 | 21025 | 21027 | 21051 | 21226 | 21229 | 21230 | 21231 | 21317 | 21318 | 21319 | 21344 | 21383 | 21390 | 21391
| Building Location | Montreal, QC | Lachine, QC | Pointe-Claire, QC | Pointe-Claire, QC | Montreal, QC | Dorval, QC | Montreal, QC | Saint-Laurent, QC | Dorval, QC | Montreal, QC | Saint-Laurent, QC | Pointe-Claire, QC | Montreal | Laval | Lachine | Montreal | Montreal | Montreal | Montreal | Montreal | Montreal | Longueuil | Montreal | Montreal | Montreal | Montreal
| Address | 2580 Dollard Avenue | 1600 50th Avenue | 5500 Trans-Canada Highway | 117 Hymus Boulevard | 7101 Notre-Dame Street East | 2900 Avenue Andre | 7350 Trans-Canada Highway | 2520 Marie-Curie | 1177-1185 55e Ave | 5685 Rue Cypihot | 3665 Boulevard Poirier | 7800 Transcanada | 8000 Blaise-Pascal | 1313 Autoroute Chomedey | 1125 50th Avenue | 5000 rue Fairway & 1645 50e Avenue | 333 Chemin du Tremblay | 1500 rue Nobel | 2000 32e Avenue | 1825 - 1865 32e Avenue | 1876 - 1936 32e Avenue | 2350 de la Province | 2995 Le Corbusier | 700 McCaffrey Road | 401 Rue Marie Curie | 3055 Rue Anderson
| Owner | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Summit Industrial (Quebec) Inc. | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc | Dream Industrial Canada Solar Inc
| Building SQFT | 89000 | 241599 | 511848 | 211346 | 611434 | 111103 | 115000 | 154374 | 155892 | 157208 | 534111 | 380553 | 326345 | 165000 | 210710 | 108292 | 86842 | 82051 | 81288 | 71616 | 84659 | 222464 | 130736 | 79875 | 753072 | 365694
| Year Built | 1973 | 1968 | 1958 | 2004 | 1947 | 1975 | 1972 | 1990 | 1990 | 1980 | 2003 | 1964 | 1993 | 1999 | 2000 | 1978 | 1987 | 1989 | 1985 | 1986 | 1987 | 1967 | 1975 | 1975 | 2005 | 2003
| Maximum estimated Rooftop PV System Size (kW DC) | 1113.12 | 3402.8 | 5900.26 | 2789.865 | 6739.47 | 1436.288 | 1122.3 | 1951.67 | 1929.42 | 2044.305 | 6100.92 | 4547.07 | 2392.2 | 2241.27 | 2168.86 | 1197.38 | 1134.965 | 1050.39 | 1074.83 | 1444.23 | 1114.635 | 2757.85 | 1506.89 | 1082.145 | 9767.52 | 4860.996
| Estimated Rooftop PV System Size (kW AC) | 695.7 | 2126.75 | 3687.6625 | 1743.6656 | 4212.1687 | 897.68 | 701.4375 | 1219.7938 | 1205.8875 | 1277.6906 | 3813.075 | 2841.9188 | 1495.125 | 1400.7938 | 1355.5375 | 748.3625 | 709.3531 | 656.4937 | 671.7687 | 902.6437 | 696.6469 | 1723.6562 | 941.8062 | 676.3406 | 6104.7 | 3038.1225
| Draft Layout size (DC) | 845.3 | 2705.6 | 4885 | 2448.1 | 6055 | 1331.9 | 907.5 | 1650 | 1510 | 1813.8 | 6205.6 | 4237.5 | 3282.5 | 1774.4 | 1906.25 | 1008.8 | 906.3 | 875 |  |  |  | 2562.5 | 1251.9 | 899.4 | 8865.6 | 4261.9
| Roof Condition and Capex | $1.3M budgeted in 2025-2027 for replacement. | $5.3M budgeted in 2027-2029 for replacement. | $3.7M budgeted in 2027-2029 for replacement. | $3.8M budgeted in 2027 for replacement. | 50% of roof is less than years old. | 30% of roof is less than 6 years old. $660k budgeted in 2025 for replacement. | $2M budgeted in 2027 for replacement. | 100% of roof is under 8 years old. | $2.6M budgeted in 2026-2027 for replacement. | $2.3M budgeted in 2029 for replacement. | Tenant is expected to complete full roof replacement in 2026. | 100% of roof is under 8 years old. | $1.5M budgeted in 2026-2028 for replacement. | $850k budgeted in 2025 for replacement. | $2.9M budgeted in 2032 for replacement. | Half of roof is new. $215k budgeted in 2026 for an additional 1/6th of roof. This brings total new roof to 70,000 ft2. | 80% of roof is under 8 years old. $144k budgeted in 2026 for additional roof replacement. | 85% of roof is under 7 years old. | 100% of roof is under 7 years old. | $630k budgeted in 2026-2031 for replacement. | $935k budgeted in 2030-2032 for replacement. | $1.4M budgeted for 60% of roof in 2030-2031. | 18% of roof area is 4 years old. $1.1M budgeted in 2026-2030 for replacement. | 40% is under 7 years old. $625k budgeted in 2027-2028 for replacement. | 30% of roof is under 4 years old. $7.5M budgeted in 2028-2030 for replacement. | $2M budgeted in 2026-2029 for replacement.
| Roof Type | [15 empty] | 1 - 16720 ft2 - BUR - Installed ; 2 - 13741 ft2 - BUR - Installed ; 3 - 14194 ft2 - BUR - Installed ; 4 - 13741 ft2 - Modified bitumen - Installed ; 5 - 14194 ft2 - Modified bitumen - Installed ; 6 - 9595 ft2 - - Installed ; 7 - 9500 ft2 - - Installed | A - 9242 ft2 - - Installed 2022; B - 10980 ft2 - - Installed 2001; C - 12929 ft2 - Modified bitumen - Installed 2014; D - 12929 ft2 - - Installed 2015; E - 13200 ft2 - - Installed 2022; F - 10945 ft2 - Modified bitumen - Installed 2018; G - 15575 ft2 - Modified bitumen - Installed 2018 | A - 11492 ft2 - Modified bitumen - Installed 2022; B - 18260 ft2 - Modified bitumen - Installed 2020; C - 17104 ft2 - Modified bitumen - Installed 2015; D - 17704 ft2 - Modified bitumen - Installed 2018; E - 18341 ft2 - Modified bitumen - Installed 2022 | A - ft2 - - Installed 2019; B - ft2 - - Installed 2019; C - ft2 - - Installed 2020; D - ft2 - - Installed 2021; E - ft2 - - Installed 2021; F - ft2 - - Installed 2021 | A - 8789 ft2 - Modified bitumen - Installed 2003; B - 11238 ft2 - - Installed ; C - 10187 ft2 - - Installed ; D - 10542 ft2 - Modified bitumen - Installed 2003; E - 14301 ft2 - Modified bitumen - Installed 2003; F - 14285 ft2 - Modified bitumen - Installed 2003 | A - 11170 ft2 - ? - Installed 2023; B - 12431 ft2 - ? - Installed 2021; C - 10000 ft2 - ? - Installed 2005; D - 11194 ft2 - ? - Installed 2005; E - 11013 ft2 - ? - Installed 2005; F - 11240 ft2 - ? - Installed 2005; G - 16964 ft2 - ? - Installed 2005 | A - ft2 - - Installed ; B - 60000 ft2 - - Installed ; C - 88000 ft2 - - Installed | 1 - 5304 ft2 - BUR - Installed 2021; 1.1 - 9900 ft2 - BUR - Installed 2006; 1.2 - 10201 ft2 - BUR - Installed 2006; 1.3 - 10000 ft2 - BUR - Installed 2003; 1.4 - 7800 ft2 - BUR - Installed 2021; 1.5 - 15197 ft2 - BUR - Installed 2001; 1.6 - 15352 ft2 - BUR - Installed 2000; 1.7 - 15200 ft2 - BUR - Installed 2006; 2 - 7722 ft2 - BUR - Installed 2021; 2.1 - 7623 ft2 - BUR - Installed 2006; 2.2 - 10692 ft2 - BUR - Installed 2000 |  | 1 - 96213 ft2 - - Installed 2022; 2 - 183920 ft2 - Modified bitumen - Installed 2005; 3 - 157994 ft2 - Modified bitumen - Installed 2005; 4 - 161556 ft2 - Modified bitumen - Installed 2005; 5 - 129663 ft2 - - Installed 2021; A - 11508 ft2 - ? - Installed 2005; B - 3502 ft2 - ? - Installed 2005; C - 3019 ft2 - ? - Installed 2005
| Roof Comments | About half of roof is due for replacement. $167k budgeted in 2025 for BUR type roof 11,935 sf roof area 1.7A. $1.144M budgeted in 2027 for BUR type roof 44,775 sf roof area 1.0,1.1,1.2 &1.6. | Was tenant managed but now vacant. $400k budgeted in 2027 for BUR type roof 15,325 sf roof area 1.9 & 2.6. $4.9M budgeted in 2029 for BUR type roof 11,352 sf roof area 1.0, 1.1,CA1 AND BUR type roof 172,000 sf roof area 1.0, 1.1,1.10 &1.11 & 1.2 to 1.7 | Basins E1, H3, M1 and M2 were replaced in 2022. $2.1M budgeted in 2027 for Mod-bit type roof 38,622 sf roof area H1,H2, H6, H8 Single Ply TPO type roof 46,139 sf roof area J,L,N. $830k budgeted in 2028 for BUR type roof 2,658 sf roof area B1, B6; Mod-bit type roof 29,928 sf roof area H9-H11, H13,I1-I3, & I; Single Ply TPO type roof 2,812 sf roof area K. $715k budgeted in 2029 for BUR type roof 9,819 sf roof area B2-B5, D1 & E2 Mod-bit type roof 18,174 sf roof area H4, H5, H7, H12. | $3.8M budgeted in 2027 for full roof (EPDM-LLB type roof 209,856 sf roof area 1.0) | 2020 - Roof membrane replacement of areas 2.0, 2.1,2.2,2.3,3.0,3.2,4.08,4.13,4.15 and 4.16 | 2019 - replacement of areas 1.4 and 1.5. $660k budgeted in 2025 for BUR type roof 32,000 sf roof areas 1.0 &1.1 | $2M budgeted in 2027 for whole roof | Roof membrane replaced in 2018 | 4 Yrs - Basin A15 11 Yrs - A-4 A-9 and A-10 12 Yrs A-14 and A-15 14 Yrs- Basin A15 $2.6M budgeted in 2026 and 2027 for BUR type roof 64,873 sf Roof Areas: A7, A9 to A14 & A18 AND BUR type roof 21,863 sf roof areas A1 to A4 & A17 AND EPDM type roof 59,691 sf roof areas A5-6, A8 & A16 | Replacement required before solar installation. $2.3M budgeted in 2029 for SPTPO type roof 104,595 roof area 1.0 to 1.3 | Tenant started roof replacememtn in 2023 and expects to complete the 4 phases in 2026. As it's a tenant managed roof, can we put solar on top? Will we need to reimburse them for the recent upgrades or pay roof rent or what? | Roof area 1.0-1.11 and 3.1/3.1 were replaced in approximately 2019. Roof area 2.0 was installed in 2022-2023 as part of a renovation/addition project. | Unknown - Sept 2024 roof report mentions lots of deficiencies but not age of roof and overall condition. We have $1.5M budgeted (105k ft2) in 2026-2028 capex plan. Should be enough to support new roof. Vacant. | Unknown - Nov 2024 roof report mentions lots of deficiencies but not age of roof and overall condition. We have $850k budgeted in 2026 capex plan for full roof | Unknown - but we have $2.9M budgeted in 2032. this site would be a good candidate if roof replacement is accelerated. | Unknown - $215k budgeted in 2026 capex plan for 1/6th of building. Appears like half of the roof is newish TPO. This would bring total good roof area to ~70,000 ft2 | 57% of roof (48962 ft2) under 7 years old, 36% of total roof is 7 years old (now or never). Rest of roof is between 10-24 years old. $144K BUDGETED IN 2026 - CAPEX PLAN. | Most of the roof is under 7 years old (~85%). | The entire roof is under 7 years old. | Would need a roof replacement as roof is at the end of its life. 2026-31 - $630k (47k ft2) budgeted for replacement | 30% of the roof (23601 ft2) is between 2-4 years. The rest 70% is 20 years old. 2030-32 - $935k (60k ft2) budgeted (C,D,E,F,G) | 2030-31 - $1.4M budgeted for 130k ft2 of roof | 18.1 % of roof area (20,826 ft2) is 4 years old, 45% (51241 ft2) is above 20 years and would need to be replaced due to end of life. To note, 37% of the roof (42,924 ft2) is currently 19 years old, and will join the 20+ years (category 2 shortly). $1.1M BUDGETED IN 2026-2030 - CAPEX PLAN. | Unknown - 40% apprears newish. 60% appears old (but in ok condition). $625k budgeted in 2027-2028 capex plan (52k ft2). | 30 % of roof is between 3-4 years (225,976 ft2); the rest (521499 ft2) is 20 years old. 2028-2030 - $7.5m budgeted for 450k ft2 roof replacement | "The specific age of each pool was not provided to us, but it appears that these roofs date from around 2003. This has not been confirmed by La Pointe du conseil inc. Pools 1 to 27 are currently approximately 21 years old. Leaks reportedly occurred this winter, and a contractor selected by Dream undertook temporary caulking work on two pools specifically, namely pools B3 and B13." $2M budgeted in 2026-2029 capex plan.
Structural | Conclusion | Need to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | For 1987 Expansion, need to replace BUR roof with TPO or equiv. For the original building, we need to either remove half of the rock ballast OR replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | For 2006 expansion, we either need to complete some reinforcement OR mechanically fasten the solar panels. For the original building, need to replace BUR roof with TPO or equiv; some of original building does not have BUR ballast, so can support solar as is. Need to confirm roof budget is sufficient for whole roof. Also need to inspect Siporex panels for structural | lowereing ballast on epdm would work but roof replacement budgeted too (could switch to lighter roof material). Need to confirm if roof budget is sufficient for whole roof. | Bldg #1 - can support solar as is. Bldg #2 - would need to replace 3/4" of rock ballast with 1/4" rock ballast (probably not best practice) OR replace with lighter roof. When is replacement budgeted for? Bldg #3 - some is ok as is; some requires replacement with lighter roof. When is replacement budgeted for? Bldg #4 - some structural concerns as is needs to be investigated. requires replacement with lighter roof. When is replacement budgeted for | would need to replace 1.5" of rock ballast with 0.75" rock ballast OR replace with lighter roof. Need to confirm roof budget is sufficient for whole roof. | Need to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | All good as is | Half of roof can support solar as is. The other half needs to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | Need to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | would need to replace 2" of rock ballast with 0.75" rock ballast (which is ok as it's EPDM) OR replace with lighter roof. Need to confirm tenant's timing for replacement and ensure they install lighter roof. | Expansion can support solar as is; but original needs to replace BUR roof with TPO or equiv. When is replacement budgeted for? We need to cover whole roof in solar to meet minimum size requirements. | Expansion can support solar as is; but original needs to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | would need to replace 2" of rock ballast with 0.25" rock ballast (ok because it's EPDM) OR replace with lighter roof. Need to confirm roof budget is sufficient for whole roof. | would need to replace 1.5" of rock ballast with 0.25" rock ballast (ok because it's EPDM) OR replace with lighter roof. Need to confirm roof budget is sufficient for whole roof. | Half of roof can support solar with ballast removal (which is ok since it's TPO). The other half needs to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for half of roof. | Need to replace BUR roof with TPO or equiv OR mechanically fasten? Need to confirm roof budget is sufficient for whole roof. | Need to replace BUR roof with TPO or equiv OR mechanically fasten? Need to confirm roof budget is sufficient for whole roof. | rjc to see if structure could support mechanically fastened solar. Would this negatively impact roof life? | rjc to see if structure could support mechanically fastened solar. Would this negatively impact roof life? otherwise, just a small section for solar in future upon replacement. Need to confirm area that roof budget would cover. | Need to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | Expansion (EPDM) can support solar as is. The rest of building needs to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | For the new roof, we might be able to mechanically fasten? For the balance of the roof, Need to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | For the new roof, we might be able to mechanically fasten? For the balance of the roof, Need to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | Expansions (TPO) can support solar as is. The rest of building needs to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof. | Expansion (TPO) can support solar as is. The rest of building needs to replace BUR roof with TPO or equiv. Need to confirm roof budget is sufficient for whole roof.
| RJC Comments | This conclusion is correct to achieve an additional load allocation for solar panels. | These conclusions are correct to achieve an additional load allocation for solar panels. | Conclusion for original building is recommended further structural investigation. Change to lighter roof may be possible to permit solar based on investigation results. For the 2006 expansion, the conclusion is correct as reinforcement is required to achieve an additional load allocation for solar panels. Reinforcement is needed for either mechanically fastened or ballasted panels. Upon review of available documentation, there is also a 1996 expansion with Mod-Bit. This was not evaluated previously and should be subject to further verification. Conduct structural inspection prior | This conclusion is correct to achieve an additional load allocation for solar panels. | Follow Figure 3 from report for building naming. In ProsPec roof buildings report #2, #3 and #4 are referred to separated buildings excluded from RJC's scope of work and report. Conclusions as stated above for Bldg #1 and #3 are correct to achieve an additional load allocation for solar panels. Conclusion for Bldg #2 is roof replacement only. Conclusion for Bldg #4 is recommended further structural investigation. Change to lighter roof may be possible to permit solar based on investigation results. | Not correct. The only viable option is to replace BUR roof with lighter roof. To replace ballast thickness is not sufficient for this case due to current state of joists by structural analysis. | This conclusion is correct to achieve an additional load allocation for solar panels. | This conclusion is correct. | These conclusions are correct. | This conclusion is not correct. Roof type is already a TPO system. Original design loads are higher than required for this roof type. Thus, low density PV panels are possible. | These conclusions are correct to achieve an additional load allocation for solar panels. | These conclusions are correct. Original roof was verified with mechanically fastened and our recommendation does not change with regards to needing to replace the roof to achieve an additional allocation for solar panels. | These conclusions are correct. | These conclusions are correct to achieve an additional load allocation for solar panels. | These conclusions are correct to achieve an additional load allocation for solar panels. | These conclusions are correct to achieve an additional load allocation for solar panels. | Roof was verified with mechanically fastened and our recommendation does not change with regards to needing to replace the roof to achieve an additional allocation for solar panels. | Roof was verified with mechanically fastened and our recommendation does not change with regards to needing to replace the roof to achieve an additional allocation for solar panels. | Roof was verified with mechanically fastened and our recommendation does not change with regards to needing to replace the roof to achieve an additional allocation for solar panels. | Roof was verified with mechanically fastened and our recommendation does not change with regards to needing to replace the roof to achieve an additional allocation for solar panels. | This conclusion is correct to achieve an additional load allocation for solar panels. | These conclusions are correct. | To our knowledge, there is only one roof type. The conclusion is to replace BUR to TPO or equivalent. Roof was verified with mechanically fastened and our recommendation does not change with regards to needing to replace the roof to achieve an additional allocation for solar panels. | To our knowledge, there is only one roof type. The conclusion is to replace BUR to TPO or equivalent. Roof was verified with mechanically fastened and our recommendation does not change with regards to needing to replace the roof to achieve an additional allocation for solar panels. | These conclusions are correct. | These conclusions are correct
| Pass | yes | yes | Partial | yes | yes | yes | yes | yes | yes | yes | yes | Yes | yes | yes | partial | yes | yes | yes | yes | yes | yes | partial | yes | yes | yes | partial
| Preliminary Capacity | 0.36 | 0.36-0.45 | 0.25-0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.25 | 0.25-0.36 | 0.25 | 0.48 | 0.36 | 0.3-0.36 | 0.48 | 0.36 | 0.36 | 0.36 | 0.36 |  |  |  | 0.36 | 0.36 | 0.36 | 0.25 | 0.36
| Final report Capacity | 0.4* | 0.28-0.90 | 0.25 | 0.55-0.75 | 0.25,0.25,0.36-0.6,0.25 | 0.6* | 0.36-0.60 | 0.6* | 0.36 - 0.6 | 0.25* | 0.6-0.9 | 0.25-0.36-0.6* | 0.3-0.4-0.6 | 0.35-0.55 | 0.4-0.6 | 0.36-0.6 | 0.36-0.60 | 0.36-0.6 | 0.36-0.6 | 0.36-0.6 | 0.36-0.6 | 0.36-0.6 | 0.36-0.6 | 0.36-.60 | 0.25-0.28* | 0.25-0.48-0.75
| Balast Removal | yes | yes | yes | yes | yes | yes | yes | no | yes | no | yes | yes | yes | yes | yes | yes | yes | yes |  |  |  | yes | yes | yes | yes | yes
DOT results | Capacity | yes | yes | yes | yes | yes | YES | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | No | no | no | yes | yes | yes | yes | yes
| HQ substation | AQUEDUC | Laurent | DES_SOURCES | DES_SOURCE | LONGUE_POINTE | DES_SOURCES | LAURENT | DES_SOURCES | Dorval, QC | SARAGUAY | SARAGUAY | SAINT_JEAN_315_25kV | HENRI_BOURASSA | CHOMEDEY | LAURENT | LAURENT | DU_Tremblay | DU_TREMBLAY |  |  |  | DU_Tremblay | LE_CORBUSIER | Laurent | DORION | GROULX
| HQ line Identification | L23402 | l144 | L297 | L276 | l144 | L227 | L231 | L287 | L151 | L274 | L292 | L229 | L271 | L239 | L112 | L144 | L263 | L263 |  |  |  | L236 | L223 | l232 | L232 | L253
| HQ Transformer | G8P2L | x4h1h | M6D9R | S6R9R | G6R5H | M4K6H | D3Y6Y | M4Y7W | K1N9V | M3D4T | S6Y9Z | D8O1X | L2O3Q | D8F5I | M8X5S | D8C5C | D9I6U | W6M0K |  |  |  | D9I6U | K6M5Z | k2d5z | D5K1E | D3Z4B
| HQ line voltage | 347/600 | 347/600 | 25KV | 25KV | 12.5Kv | 347/600 | 347/600 | 347/600 | 347/600 | 347/600 | 347/600 | 347/600 | 347/600 | 347/600 | 347/600 | 347/600 | 347/600V | 347/600 |  |  |  | 347/600V | 347/600 | 347/600 | 347/600 | 347/600
| Distribution upgrade | 460000 | 470000 | 630000 | 470000 | 610000 | 460000 | 320000 | 460000 | 320000 | 320000 | 610000 | 540000 | 420000 | 420000 | 320000 | 460000 | 460000 | 460000 |  |  |  | 460000 | 330000 | 460000 | 610000 | 340000
| substation upgrade | 0 | 2080000 |  |  | 1390000 |  |  |  | 2080000 |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  | 2080000
| Protections | 0 | [9 empty] | 530000 | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  | 530000
| Communications | 0 |  | 2590000 | 2590000 | [6 empty] | 2530000 | 2690000 | 2530000 | 2800000 | 2080000 |  | 0 |  |  |  |  | 0 |  |  |  | 2350000
| Total cost | 460000 | 2550000 | 3220000 | 3060000 | 2000000 | 460000 | 320000 | 460000 | 2400000 | 320000 | 3670000 | 3230000 | 2950000 | 3220000 | 2400000 | 460000 | 460000 | 460000 | 0 | 0 | 0 | 460000 | 330000 | 460000 | 2690000 | 3220000
| Lead time | 18 | 26 | 30 | 30 | 26 | 18 | 18 | 18 | 26 | 18 | 30 | 30 | 30 | 30 | 26 | 18 | 18 | 18 |  |  |  | 18 | 12 | 18 | 26 | 30
| completion date | 2028-11-01 | 2028-07-01 | 2029-11-01 | 2029-11-01 | 2029-07-01 | 2028-11-01 | 2028-11-01 | 2028-11-01 | 2029-07-01 | 2028-11-01 | 2029-11-01 | 2029-11-01 | 2029-11-01 | 2029-11-01 | 2029-07-01 | 2028-11-01 | 2028-11-01 | 2028-11-01 |  |  |  | 2028-11-01 | 2028-06-01 | 2028-11-01 | 2029-07-01 | 2029-11-01
| contract target date | 2028-12-01 | 2028-08-01 | 2029-12-01 | 2029-12-01 | 2029-08-01 | 2028-12-01 | 2028-12-01 | 2028-12-01 | 2029-08-01 | 2028-12-01 | 2029-12-01 | 2029-12-01 | 2029-12-01 | 2029-12-01 | 2028-08-01 | 2028-12-01 | 2028-12-01 | 2028-12-01 |  |  |  | 2028-12-01 | 2028-07-01 | 2028-12-01 | 2029-08-01 | 2029-12-01
Community engagement | Residential within 100m | y | n | n | Y |  | n | n | n | n | n | few | n | y | Y | n | n | n | n |  |  |  | n | n | n | Y | n
Community Enegagement date
Time
| Facility | 2695 Dollard | 2695 Dollard |  |  |  | 2900 Avenue Andre |  | 2900 Avenue Andre | 2695 Dollard | 2900 Avenue Andre | 2900 Avenue Andre |  | 8000 Blaise-Pascal |  | 2695 Dollard | 2695 Dollard | [8 empty] | 401 Rue Marie Curie
Attendees
Logs digitized
Electrical site visit | [5 empty] | denied | [17 empty] | rescheduled
Crews |  | 1 | 2 | 3 | 3 | 3 | 1 | 1 | 1 | 1 | 2 | 3 | 2 | 2 | 2 | 2 | 1 | 1 | 1 |  |  |  | 2 | 1 | 1 | 3 | 2
Construction completion |  | 2028-11-01 | 2028-07-02 | 2029-11-01 | 2029-11-01 | 2029-07-02 | 2028-11-01 | 2028-11-01 | 2028-11-01 | 2029-07-02 | 2028-11-01 | 2029-11-01 | 2029-11-01 | 2029-11-01 | 2029-11-01 | 2028-07-02 | 2028-11-01 | 2028-11-01 | 2028-11-01 |  |  |  | 2028-11-01 | 2028-06-01 | 2028-11-01 | 2029-07-02 | 2029-11-01
Construction Duration Days |  | 42 | 70 | 84 | 63 | 91 | n: 49; n: 42; n: 63; n: 63; n: 63; few: 91
Est Construciton start |  | 2028-09-20 | 2028-04-23 | 2029-08-09 | 2029-08-30 | 2029-04-02 | 2028-09-13 | 2028-09-20 | 2028-08-30 | 2029-04-30 | 2028-08-30 | 2029-08-02 | 2029-11-01 | 2029-11-01 | 2029-11-01 | 2028-07-02 | 2028-11-01 | 2028-11-01 | 2028-11-01 |  |  |  | 2028-11-01 | 2028-06-01 | 2028-11-01 | 2029-07-02 | 2029-11-01
Pre construction roof prep |  | 2028-08-21 | 2028-03-24 | 2029-07-10 | 2029-07-31 | 2029-03-03 | 2028-08-14 | 2028-08-21 | 2028-07-31 | 2029-03-31 | 2028-07-31 | 2029-07-03 | 2029-10-02 | 2029-10-02 | 2029-10-02 | 2028-06-02 | 2028-10-02 | 2028-10-02 | 2028-10-02 |  |  |  | 2028-10-02 | 2028-05-02 | 2028-10-02 | 2029-06-02 | 2029-10-02
Formulas:
Montreal, QC = C45-[Montreal, QC, row above]
Montreal, QC = [Montreal, QC, row above]-30
Lachine, QC = D45-[Lachine, QC, row above]
Lachine, QC = [Lachine, QC, row above]-30
Note on B10: James Pagonis: DOt approved size
Note on B23: James Pagonis: Add dot reference #s
Note on B24: James Pagonis: Clarify Connection point